Include the following information on the project drawings. See DCSM sections 2.4 and 2.7 for additional details on drawings.

**Instructions**:

Indicate your response to each item in the checklist. Select ‘Yes’ if the checklist item has been completed in full. Select ‘No’ or ‘N/A’ if that item is not included or not required for the specific project. Explain why that item has not been included in the submittal.

| **RESPONSE** | **REQUIREMENTS** |
| --- | --- |
| Choose an item. | Show a north arrow and provide drawing scale. Use ⅛" scale minimum for floor plans. |
| Choose an item. | Provide plans for each floor (with room numbers) noting locations and types of fixtures, water supply and distribution, sanitary drainage, and special piping. |
| Choose an item. | Provide riser diagrams indicating fixtures, water supply and distribution, sanitary drainage, and special piping. |
| Choose an item. | Provide location of water supply and distribution, sanitary sewer and drainage, storm sewer and drainage, and sprinkler services to the building. |
| Choose an item. | Show routing of main supply and distribution lines with tentative sizes. Include drainage and venting. |
| Choose an item. | Show fixture locations, types, and a tentative schedule. |
| Choose an item. | Provide plumbing fixture schedules showing designations, connection sizes, and mounting heights of accessible fixtures. Locate flush valve handles on the wide side of the accessible stall. |
| Choose an item. | Provide locations, sizes, and types of water heaters, heat exchangers, storage tanks, flues, etc. |
| Choose an item. | Provide the fuel gas piping layout and connected load, if applicable. |
| Choose an item. | Provide locations for special plumbing wastes, traps and interceptors, and medical gases. |
| Choose an item. | Indicate items to be demolished as part of renovation projects. |
| Choose an item. | Provide plans indicating roof drains and areas served by each in square feet, piping, and sizes. |
| Choose an item. | Provide details of connections at water heaters, air compressors, and roof drain installation. |
| Choose an item. | Provide equipment schedules for water heaters, air compressors, air dryers, and drains. |
| Choose an item. | Provide configuration and sizes of piping systems. |
| Choose an item. | Show locations of hot water and cold water shut-off gate valves for each toilet room. |
| Choose an item. | Provide dimensioned location and type or schedule number of each plumbing fixture with clearances as required to comply with the ADA Standards for Accessible Design, latest edition. |
| Choose an item. | Provide typical details for attaching wall-hung fixtures to walls. |
| Choose an item. | Indicate whether piping is run above or below ground, floors, and ceilings and whether it is concealed or exposed. |
| Choose an item. | Provide the capacity and operating characteristics of each item of equipment. |
| Choose an item. | Provide locations and details for special supports for piping. |
| Choose an item. | Provide locations, sizes, and types of cleanouts. |
| Choose an item. | Provide locations, sizes, and typical details for extended rim floor drains. |
| Choose an item. | Provide detail or sections through each type of roof drain, floor sink, and grease interceptor or separator. |
| Choose an item. | Indicate roof drain/roof leader piping locations and sizes. |
| Choose an item. | Show location of acid-resistant DWV piping, cleanouts, traps, drains, and accessories. |
| Choose an item. | Confirm that cleanouts in crawl spaces or the exterior of buildings shall be not less than 3 feet from the building wall. |
| Choose an item. | Confirm that exterior buried piping shall not run parallel within 5 feet of exterior building wall. |
| Choose an item. | Provide location and size of water hammer arresters. |
| Choose an item. | Provide ranges and accuracies for gauges and thermometers. |
| Choose an item. | Show capacity, size, bypass valves, and piping for water meters. Provide detail of water meter box (coordinate with serving utility entity). |
| Choose an item. | Provide locations and sizes of access panels for valves. |
| Choose an item. | Provide details of pipe penetrations in outside walls. |